E50H2A

Compact Rope Style Power and Energy Meter

With BACnet Communication

The power meter shall be fully electronic with multi-line backlit LCD display showing measured parameters as well as alarm functions and pulse output.

The power meter shall perform the following measurements:

Accumulated Real Energy (kWh) for each phase and total of all phases

Accumulated Reactive Energy (kVARh) and Apparent Energy (kVAh) totals for all phases

Net Present Demand for Real (kW), Reactive (kVAR) and Apparent (kVA) Power over a user-specified interval (block or sliding window)

Maximum (Peak) Real (kW), Reactive (kVAR) and Apparent (kVA) Demand Intervals

Instantaneous Real (kW), Reactive (kVAR) and Apparent Power (kVA), by phase and in total

Current (amps) for each phase and average of all phases

Phase-to-phase voltage for each phase and average of all phase pairs

Phase-to-neutral voltage for each phase pair and average of all phases

Power factor for each phase and average of all phases

AC frequency

The power meter shall communicate using the BACnet MS/TP protocol at speeds from 9600 to 115,200 baud (no parity).  The meter shall provide a BACnet Device object, a set of writable Analog_Value objects for remote configuration, a set of Analog_Input objects to provide access to scaled 32-bit measurement values and their unit types, and a set of Binary_Input objects for indicating individual alarm conditions.

The meter shall be UL/CUL listed to the latest applicable safety standards.

Power meter models shall accept voltage input over the range of 90 to 600 VAC (50 or 60 Hz).

The power meter shall accept 0 to 0.333VAC input from up to three current transducers (U018 Rope Style CTs only) from 20 to 5000 amps.

The measured energy consumption shall be retained in non-volatile memory for the life of the product warranty.

The power meter shall have demand measurement programmable for up to 6 sub-intervals of 10 seconds to 546 minutes duration.

Meter shall be optionally available in an outdoor NEMA 4X enclosure.

The power meter shall operate from -30°C to +70°C.

The power meter shall have dimensions not exceeding 4.2” x 3.6” x 2.3”.

The power meter shall be Veris E50H2A or equivalent.

The power meter shall meet both ANSI C12.20 .5% and IEC 62053-22 Class .5S real power and energy accuracy specifications.

The power meter shall meet IEC 62053-22 Class 2 reactive power and energy accuracy specifications.

The power meter shall be configurable for operation on Single Phase (AN or AB), Split Phase (ABN), Delta (ABC), and Wye (ABCN) systems.

The power meter shall have automatic phase reversal compensation such that it is insensitive to the CT’s load orientation.

The power meter shall have separate control power inputs such that is may be powered from a different service than it measures.

The power meter shall have Phase Loss Alarm contacts with a user configurable phase loss threshold.

The power meter shall have a user-configurable Pulse Contact input to support measurement of other related energy (Gas, Water, Steam, etc.) via BACnet using a simple pulse-output transducer.

The power meter shall be configurable for use with Potential Transformers to 5000 volts.

The power meter shall support warnings for low power factor (phase current or voltage miss-wired), current over range, voltage over range, and frequency out of range.

The product shall have a 5-year warranty.